## Slide 1: Introduction
Controls engineer with multi-domain system experience
Focus: diagnosing non-obvious and intermittent failures
Approach: structured RCA + real data

## Slide 2: Field Experience
Offshore hydraulic top drive systems
Industrial automation and commissioning
Multi-domain: mechanical, hydraulic, electrical, controls

## Slide 3: Project: Fire Training Simulator
Gas + air + ignition system
Safety interlocks and sequencing
Commissioning and reliability responsibility

## Slide 4: RCA Philosophy
Do not assume PLC is the issue
Separate symptom vs root cause
Validate each domain independently

## Slide 5: RCA Framework
Define problem
Isolate domains
Collect real data
Validate root cause
Fix + prevent recurrence

## Slide 6: Case 1: Problem
Intermittent ignition failure
Multiple retries needed
Control signals appeared correct

## Slide 7: Case 1: Root Cause
Clogged air filter reduced airflow
Insufficient pressure during ignition
System appeared random due to pressure recovery

## Slide 8: Case 1: Solution
Replaced filter
Added pressure transmitter
Added SCADA monitoring + maintenance schedule

## Slide 9: Key Lesson
No instrumentation = no visibility
Process issues can mimic control failures

## Slide 10: Case 2: Problem
Intermittent shutdown
No logging available
Occurs randomly

## Slide 11: Case 2: Strategy
Built 24/7 Python monitoring
Captured all stop conditions and permissives
Real-time alert via Slack

## Slide 12: Case 2: Root Cause
Intermittent manual button trigger
Not visible in PLC trending
Captured via external monitoring

## Slide 13: Comparison
Case 1: Process issue → instrumentation
Case 2: Intermittent issue → monitoring
Same principle: get real data

## Slide 14: Relevance to Industry
Multi-domain systems (gas, thermal, motion)
Need structured RCA
Avoid assumptions, rely on data

## Slide 15: Closing
Focus: control decisions affecting physical systems
Strength: diagnosing non-obvious failures
Approach: structured, data-driven engineering